## Slide 1
(CERN EDMS Document N.1099646)

## Slide 8
Random vibrations and FEM
Full 3D mesh in conjuction with the Random Vibration Solver Module:
Huge model with ~300k elements,
Very Long Computing time ~ 12 hours
Not suitable for parametric study, i.e. changes of geometry or material properties
Solver as Black Box, hard to have full control of the algorithm
Harmonic Analysis -> Determination of the Transfer Functions
Modal analysis of the full 3D mesh, still very long, computing time waste on several uniteresting local modes
Simplified 3D or 2D model representing the master degree of interest: fast, reliable, flexible. One need to know exactly which global mode are of interest.

## Slide 9
9
Random vibrations study
X
=
Ground Motion PSD
Frequency Response Function
2
Analytically
FEA
The Model requires the Ground Motion Spectrum P(f) and the Frequency Response Function H(f) of the structure

## Slide 10
20 m
18 m
2 m
Reinforced concrete Slab
Four support lines for 4’000 tons each
10kt Anti-seismic supports
Steel plate 30 mm at the bottom
Steel re-bars 16mm2
Total mass 1800 t

## Slide 11
CMS Platform (as built)
2200
20.5 m
Iron re-bars (equivalent th. 25 mm)
Iron re-bars (equivalent th. 25 mm)
Concrete, 2150 mm
Total thick. 2.2 m
Plate Model: zero thickness with bending stiffness around the middle plane

## Slide 12
Bencmark with static test done on the platform
Dummy load = 2500 tons,
Weight of the platform = 1780 tons
Max sag at the center = 3.5 mm
N.B. = Platform Simply supported on the edges

## Slide 13
Mode 1
Mode 5
Mode 4
Mode 3
Mode 2
Mode FREQ
1 20.17
2 41.12
3 53.24
4 72.76
5 73.28
6 95.85

## Slide 14
Transfer Function - Middle Point (Geophone N.3)
0.707*Max. Ampl
(1-g)*fn
(1+g)*fn
Critical damping ~ g = (f2 – f1)/2* fn
g = 6.8%

## Slide 15
Resonance at ~20 Hz
Simulations vs. Measured PSD (Platform Center)
Peaks 80 and 90 Hz

## Slide 16
Integrated Displacement (r.m.s.)