## 110721Full
July 21 2011
WATER AND AIR HEAT LOAD for Revised DRFS Full Version
MAIN LINAC - ELECTRON & POSITRON | [13 empty] | OIL(k litter)
To Dirty Water
[5 empty] | Group A | [9 empty] | Group B | GroupC | Group D | Group E | Average
Cavity Mediam Gradient (MV/m) |  |  |  |  | 36.8 | [9 empty] | 34.1 | 31.5 | 28.9 | 26.3 | 31.52 |  | S. Fukuda 21-7-11
Pulse Width(ms) |  |  |  |  | 1.8 | [9 empty] | 1.76 | 1.71 | 1.66 | 1.61 | 1.708 |  | S. Fukuda 21-7-11
AV. Power Increase Factor |  |  |  |  | 1.3445 | [9 empty] | 1.2181 | 1.0933 | 0.97371 | 0.85942 | 1.0978 |  | S. Fukuda 21-7-11
Beam power(kW) |  |  |  |  | 43.3388 | [9 empty] | 40.1591 | 37.0971 | 34.0351 | 30.9731 | 37.1207 |  | S. Fukuda 21-7-11
Components |  | Quantity Per 38m | Location | Total Heat Load (KW) | Average Heat Load (KW) | Heat Load to Water (KW) | Supply Temp (variation) ( C ) | Delta Temperature (C delta) | Water Flow (l / min) | Maximum Allowable Pressure (Bar) | Typical (water) pressure drop Bar | Acceptable Temp Variation delta C | Max Space Temp ( C ) |  | Average Heat Load (KW) | Average Heat Load (KW) | Average Heat Load (KW) | Average Heat Load (KW) |  | Source | Source
Non-RF Components
LCW Skid Pump 1 per 4 rf -Motor/Feeder Loss |  | 0.25 | Service Tunnel | 0.6 | 0.6 | 0 | N/A | N/A |  | N/A | N/A | None
I^2R Loss and Motor Loss (misc) |  | 1 | Service Tunnel | 0 | 22.9247
Fancoils (5 ton Chilled Water) 1.5 Hp |  | 2 | Service Tunnel | 2.9057 | 2.9057 | 0 | N/A | N/A |  | N/A | N/A | None
Rack Water Skid |  | 0.25 | Service Tunnel | 0.20431 | 0.20431 | 0 | N/A | N/A |  | N/A | N/A | None
Lighting Heat Dissipation ~1.3W/sf |  |  | Service Tunnel | 1.652 | 1.652 | 0 | N/A | N/A |  | N/A | N/A | None
AC Pwr Transformer 34.5-.48 kV |  | 0.25 | Service Tunnel | 2 | 2 | 0 | N/A | N/A |  | N/A | N/A | None
Emerg. AC Pwr Transformer 34.5-.48 kV |  |  | Service Tunnel | 1 | 1 | 0 | N/A | N/A |  | N/A | N/A | None
RF Components
--- High Voltage Circuit Breaker：VCB (6.6 kV) --- | Rack | 1/38 m | Single Tunnel | [9 empty] | 85 F (a) | [6 empty] | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
--- High Voltage Circuit Breaker：VCB (6.6 kV) ---Spare | Rack | 0.5/38 m | Single Tunnel | [16 empty] | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Step Down Transformer from 6.6kV to 420V/98% 4kW Spare | Tank | 0.5/38 m | Single Tunnel |  | 2 | [8 empty] | 0.4 | 2 | 2 | 2 | 2 | 2.08 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Step Down Transformer from 6.6kV to 420V/ 95% 10kW | Tank | 1/38 m | Single Tunnel |  | 14.1168 | [8 empty] | 0.2 | 12.7903 | 11.4795 | 10.224 | 9.0239 | 11.5669 | S. Fukuda 11-23-10 Adjusted+5% | S. Fukuda 21-7-11
Switching Regulator Power Supply 420V/ 85% 30kW | Rack | 1/38 m | Single Tunnel |  | 42.3503 | [8 empty] | 0.06 | 38.371 | 34.4384 | 30.672 | 27.0718 | 34.5927 | S. Fukuda 11-23-10 Adjusted+5% Efficency up to 85% same as RDR | S. Fukuda 21-7-11
Switching Regulator Power Supply 420V/ Spare 10% 2kW | Rack | 0.5/38 m | Single Tunnel |  | 1 | [8 empty] | 0.03 | 1 | 1 | 1 | 1 | 1.006 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Capacitor Limitter Registor 3.8kW |  | 1/38 m | Single Tunnel |  | 5.3644 | [8 empty] | 0.36 | 4.8603 | 4.3622 | 3.8851 | 3.4291 | 4.4522 | S. Fukuda 11-23-10 Adjusted+5% | S. Fukuda 21-7-11
Capacitor Limitter Registor Spare |  | 0.5/38 m | Single Tunnel |  | 0 | [8 empty] | 0.18 | 0 | 0 | 0 | 0 | 0.036 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Bouncer Coil 0.5kW |  | 1/38 m | Single Tunnel |  | 0.67223 | [8 empty] | 0.17 | 0.60906 | 0.54664 | 0.48686 | 0.42971 | 0.5829 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Bouncer Coil 0.5kW Spare |  | 0.5/38 m | Single Tunnel |  | 0 | [8 empty] | 0.085 | 0 | 0 | 0 | 0 | 0.017 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Modulating Anode Modulator, 6.6 kV (Shunt 1.0 A, then 6 kW heat load) | Rack 3 | 1/38 m | Single Tunnel |  | 6.3 | [8 empty] | 0.2 | 6.3 | 6.3 | 6.3 | 6.3 | 6.34 | S. Fukuda 11-23-10 Adjusted+5% | S. Fukuda 21-7-11 |  | 72
Modulating Anode Modulator, 6.6 kV (Shunt 1.0 A, then 6 kW heat load), (Back-up) | Rack 4 | 0.5/38 m | Single Tunnel | [10 empty] | 0.1 | [5 empty] | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Crawbar 1.2mx1.2mx1.2m |  | 1/38 m | [11 empty] | 1.7 | [6 empty] | S. Fukuda 21-7-11
Crawbar 1.2mx1.2mx1.2m Spare |  | 0.5/38 m | [11 empty] | 0.85 | [6 empty] | S. Fukuda 21-7-11
Heater P/S, 200V,11A, 2.2kW 90% | Rack 3 | 1/38 m | Single Tunnel |  | 0.24 | [9 empty] | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Same as above (Back-up) | Rack 4 | 0.5/38 m | Single Tunnel | [15 empty] | 0 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Pulse Transformer |  | None | [16 empty] | 0 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Klystron Socket Tank / Gun 0.17 kW X 13=2.2kW |  | 13/38 m | Single Tunnel |  | 2.2 | [9 empty] | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Klystron Focusing x 26 (Permanent Magnet ) |  | 13/38 m | Single Tunnel |  | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Klystron Collector 4.5 kW X 13=59kW |  | 13/38 m | Single Tunnel |  | 83.77 | [9 empty] | 75.9 | 68.12 | 60.67 | 61.425 | 69.977 | S. Fukuda 11-23-10 Adjusted+5% | S. Fukuda 21-7-11
Klystron Body & Windows |  | 13/38 m | Single Tunnel |  | 3.948 | [9 empty] | 3.948 | 3.948 | 3.948 | 3.948 | 3.948 | S. Fukuda 11-23-10 Adjusted+5% | S. Fukuda 21-7-11
--- LLRF Racks --- | [18 empty] | 0 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
LLRF+Amp +Int, 200V,2.5A /5 modules | Rack 5 | 1/38 m | Single Tunnel |  | 0.35 | [9 empty] | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
LLRF+Amp +Int, 200V,1.5A /3 modules | Rack 7 | 1/38 m | Single Tunnel |  | 0.21 | [9 empty] | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
LLRF+Amp +Int, 200V,2.5A /5 modules, for full power op. | Rack 8 | 1/38 m | Single Tunnel |  | 0.35 | [9 empty] | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
LLRF+Amp +Int, 200V,2.5A /5 modules Spare |  | 0.5/38 m | Single Tunnel |  | 0.175 | [9 empty] | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
LLRF+Amp +Int, 200V,1.5A /3 modules Spare |  | 0.5/38 m | Single Tunnel |  | 0.105 | [9 empty] | 0.105 | 0.105 | 0.105 | 0.105 | 0.105 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
LLRF+Amp +Int, 200V,2.5A /5 modules,Spare |  | 0.5/38 m | Single Tunnel |  | 0.175 | 1.365 | [8 empty] | 0.175 | 0.175 | 0.175 | 0.175 | 0.448 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
--- Other Racks --- | [20 empty] | S. Fukuda 21-7-11
Timing , 200V,0.5kW | Rack 10 | 1/38 m | Single Tunnel |  | 0.5 | [9 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | H. Hayano 9-8-09 | S. Fukuda 21-7-11
Cavity , 200V,3 kW | Rack 12 | 1/38 m | Single Tunnel | 2.95 | 2.05 | [9 empty] | 2.05 | 2.05 | 2.05 | 2.05 | 2.05 | H. Hayano 9-8-09 | S. Fukuda 21-7-11
Cryogenics, 200V, 2.1 kW | Rack 14 | 1/38 m | Single Tunnel |  | 2.1 | [9 empty] | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | H. Hayano 9-8-09 | S. Fukuda 21-7-11
BPM & Mag, 200V, 5 kW | Rack 16 | 1/38 m | Single Tunnel |  | 5 | 9.65 | [8 empty] | 5 | 5 | 5 | 5 | 6.93 | H. Hayano 9-8-09 | S. Fukuda 21-7-11
--- RF Loads --- | [18 empty] | 0 |  | S. Fukuda 21-7-11
Attenuator |  | None | [16 empty] | 0 | S. Fukuda 9-4-09 | S. Fukuda 21-7-11
Waveguides in service tunnel |  | None | [16 empty] | 0 | S. Fukuda 9-4-09 | S. Fukuda 21-7-11
Waveguides in penetration |  | None | [16 empty] | 0 | S. Fukuda 9-4-09 | S. Fukuda 21-7-11
Waveguides in beam tunnel |  | 13/38 m | Single Tunnel |  | 0.8 | [9 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | S. Fukuda 5-20-10 | S. Fukuda 21-7-11
Circulator with load |  | None | [16 empty] | 0 | S. Fukuda 9-4-09 | S. Fukuda 21-7-11
RF Loads |  | 13/38 m | Single Tunnel |  | 54.84 | [9 empty] | 48.57 | 42.3 | 36.42 | 30.94 | 42.614 | S. Fukuda 5-20-10 | S. Fukuda 21-7-11
--- Other Loads --- | [18 empty] | 0 |  | S. Fukuda 21-7-11
Pulse motor for input coupler/tuner |  | (13+13)/38 m |  | 1.79 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | H. Hayano 9-8-09 | S. Fukuda 21-7-11
Vacuum Pumps |  | (1+1)/38 m |  |  | 0.63 | [9 empty] | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | H. Hayano 9-8-09 | S. Fukuda 21-7-11
HLRF related loss |  |  |  |  | 204.1137 | [9 empty] | 184.1007 | 164.2467 | 145.358 | 135.3196 | 166.9247
Fixed Loss in HLRF |  |  |  |  | 12.688 | [9 empty] | 12.688 | 12.688 | 12.688 | 12.688 | 12.728
Other Than HLRF |  |  |  |  | 11.645 | [9 empty] | 11.645 | 11.645 | 11.645 | 11.645 | 13.848
S. Fukuda 21-7-11
Subtotal RF unit Only |  |  |  |  | 229.2467 | 11.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.335 | 209.2337 | 189.3797 | 170.491 | 160.4526 | 194.3007 |  | S. Fukuda 21-7-11 | 219.7764
Total RF | [5 empty] | 11.015 | [15 empty] | 128349.4171
RF Component only Loads |  |  |  | 2.95
Note on A22: 1台当り

## 110721ReducedB Op
July 21 2011
WATER AND AIR HEAT LOAD for Revised DRFS Reduced bunch operation
MAIN LINAC - ELECTRON & POSITRON | [13 empty] | OIL(k litter)
To Dirty Water
[5 empty] | Group A | [9 empty] | Group B | GroupC | Group D | Group E | Average | Ref
Cavity Mediam Gradient (MV/m) |  |  |  |  | 36.8 | [9 empty] | 34.1 | 31.5 | 28.9 | 26.3 | 31.52 | 31.5 |  | S. Fukuda 21-7-11
Pulse Width(ms) |  |  |  |  | 2.3 | [9 empty] | 2.25 | 2.18 | 2.11 | 2.03 | 2.174 | 1.71 |  | S. Fukuda 21-7-11
AV. Power Increase Factor |  |  |  |  | 1.717 | [9 empty] | 1.5573 | 1.3938 | 1.2377 | 1.0836 | 1.3979 | 1.0006 |  | S. Fukuda 21-7-11
Beam power(kW) |  |  |  |  | 21.6694 | [9 empty] | 20.0795 | 18.5486 | 17.0176 | 17.0176 | 18.8665 | 37.1 |  | S. Fukuda 21-7-11
Components |  | Quantity Per 38m | Location | Total Heat Load (KW) | Average Heat Load (KW) | Heat Load to Water (KW) | Supply Temp (variation) ( C ) | Delta Temperature (C delta) | Water Flow (l / min) | Maximum Allowable Pressure (Bar) | Typical (water) pressure drop Bar | Acceptable Temp Variation delta C | Max Space Temp ( C ) |  | Average Heat Load (KW) | Average Heat Load (KW) | Average Heat Load (KW) | Average Heat Load (KW) |  | Average Heat Load (KW) | Source | Source
Non-RF Components
LCW Skid Pump 1 per 4 rf -Motor/Feeder Loss |  | 0.25 | Service Tunnel | 0.6 | 0.6 | 0 | N/A | N/A |  | N/A | N/A | None
I^2R Loss and Motor Loss (misc) |  | 1 | Service Tunnel | 0 | 20.0926
Fancoils (5 ton Chilled Water) 1.5 Hp |  | 2 | Service Tunnel | 2.9057 | 2.9057 | 0 | N/A | N/A |  | N/A | N/A | None
Rack Water Skid |  | 0.25 | Service Tunnel | 0.20431 | 0.20431 | 0 | N/A | N/A |  | N/A | N/A | None
Lighting Heat Dissipation ~1.3W/sf |  |  | Service Tunnel | 1.652 | 1.652 | 0 | N/A | N/A |  | N/A | N/A | None
AC Pwr Transformer 34.5-.48 kV |  | 0.25 | Service Tunnel | 2 | 2 | 0 | N/A | N/A |  | N/A | N/A | None
Emerg. AC Pwr Transformer 34.5-.48 kV |  |  | Service Tunnel | 1 | 1 | 0 | N/A | N/A |  | N/A | N/A | None
RF Components
--- High Voltage Circuit Breaker：VCB (6.6 kV) --- | Rack | 1/38 m | Single Tunnel | [9 empty] | 85 F (a) | [7 empty] | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
--- High Voltage Circuit Breaker：VCB (6.6 kV) ---Spare | Rack | 0.5/38 m | Single Tunnel | [17 empty] | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Step Down Transformer from 6.6kV to 420V/98% 4kW Spare | Tank | 0.5/38 m | Single Tunnel |  | 2 | [8 empty] | 0.4 | 2 | 2 | 2 | 2 | 2.08 | 2 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Step Down Transformer from 6.6kV to 420V/ 95% 10kW | Tank | 1/38 m | Single Tunnel |  | 18.0285 | [8 empty] | 0.2 | 16.3513 | 14.6346 | 12.9956 | 11.378 | 14.7176 | 10.506 | S. Fukuda 11-23-10 Adjusted+5% | S. Fukuda 21-7-11
Switching Regulator Power Supply 420V/ 85% 30kW | Rack | 1/38 m | Single Tunnel |  | 54.0855 | [8 empty] | 0.06 | 49.0539 | 43.9039 | 38.9867 | 34.1341 | 44.0448 | 31.518 | S. Fukuda 11-23-10 Adjusted+5% Efficency up to 85% same as RDR | S. Fukuda 21-7-11
Switching Regulator Power Supply 420V/ Spare 10% 2kW | Rack | 0.5/38 m | Single Tunnel |  | 1 | [8 empty] | 0.03 | 1 | 1 | 1 | 1 | 1.006 | 1 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Capacitor Limitter Registor 3.8kW |  | 1/38 m | Single Tunnel |  | 6.8508 | [8 empty] | 0.36 | 6.2135 | 5.5612 | 4.9383 | 4.3236 | 5.6495 | 3.9923 | S. Fukuda 11-23-10 Adjusted+5% | S. Fukuda 21-7-11
Capacitor Limitter Registor Spare |  | 0.5/38 m | Single Tunnel |  | 0 | [8 empty] | 0.18 | 0 | 0 | 0 | 0 | 0.036 | 0 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Bouncer Coil 0.5kW |  | 1/38 m | Single Tunnel |  | 0.8585 | [8 empty] | 0.17 | 0.77863 | 0.69689 | 0.61884 | 0.54181 | 0.73293 | 0.50028 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Bouncer Coil 0.5kW Spare |  | 0.5/38 m | Single Tunnel |  | 0 | [8 empty] | 0.085 | 0 | 0 | 0 | 0 | 0.017 | 0 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Modulating Anode Modulator, 6.6 kV (Shunt 1.0 A, then 6 kW heat load) | Rack 3 | 1/38 m | Single Tunnel |  | 6.3 | [8 empty] | 0.2 | 6.3 | 6.3 | 6.3 | 6.3 | 6.34 | 6.3 | S. Fukuda 11-23-10 Adjusted+5% | S. Fukuda 21-7-11 |  | 72
Modulating Anode Modulator, 6.6 kV (Shunt 1.0 A, then 6 kW heat load), (Back-up) | Rack 4 | 0.5/38 m | Single Tunnel | [10 empty] | 0.1 | [6 empty] | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Crawbar 1.2mx1.2mx1.2m |  | 1/38 m | [11 empty] | 1.7 | [7 empty] | S. Fukuda 21-7-11
Crawbar 1.2mx1.2mx1.2m Spare |  | 0.5/38 m | [11 empty] | 0.85 | [7 empty] | S. Fukuda 21-7-11
Heater P/S, 200V,11A, 2.2kW 90% | Rack 3 | 1/38 m | Single Tunnel |  | 0.24 | [9 empty] | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Same as above (Back-up) | Rack 4 | 0.5/38 m | Single Tunnel | [15 empty] | 0 |  | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Pulse Transformer |  | None | [16 empty] | 0 |  | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Klystron Socket Tank / Gun 0.17 kW X 13=2.2kW |  | 13/38 m | Single Tunnel |  | 2.2 | [9 empty] | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Klystron Focusing x 26 (Permanent Magnet ) |  | 13/38 m | Single Tunnel |  | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
Klystron Collector 4.5 kW X 13=59kW |  | 13/38 m | Single Tunnel |  | 53.52 | [9 empty] | 48.5169 | 43.4234 | 38.56 | 33.7605 | 43.5561 | 68.12 | S. Fukuda 11-23-10 Adjusted+5% | S. Fukuda 21-7-11
Klystron Body & Windows |  | 13/38 m | Single Tunnel |  | 3.948 | [9 empty] | 3.948 | 3.948 | 3.948 | 3.948 | 3.948 | 3.948 | S. Fukuda 11-23-10 Adjusted+5% | S. Fukuda 21-7-11
--- LLRF Racks --- | [18 empty] | 0 |  | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
LLRF+Amp +Int, 200V,2.5A /5 modules | Rack 5 | 1/38 m | Single Tunnel |  | 0.35 | [9 empty] | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
LLRF+Amp +Int, 200V,1.5A /3 modules | Rack 7 | 1/38 m | Single Tunnel |  | 0.21 | [9 empty] | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
LLRF+Amp +Int, 200V,2.5A /5 modules, for full power op. | Rack 8 | 1/38 m | Single Tunnel |  | 0.35 | [9 empty] | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
LLRF+Amp +Int, 200V,2.5A /5 modules Spare |  | 0.5/38 m | Single Tunnel |  | 0.175 | [9 empty] | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
LLRF+Amp +Int, 200V,1.5A /3 modules Spare |  | 0.5/38 m | Single Tunnel |  | 0.105 | [9 empty] | 0.105 | 0.105 | 0.105 | 0.105 | 0.105 | 0.105 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
LLRF+Amp +Int, 200V,2.5A /5 modules,Spare |  | 0.5/38 m | Single Tunnel |  | 0.175 | 1.365 | [8 empty] | 0.175 | 0.175 | 0.175 | 0.175 | 0.448 | 0.175 | S. Fukuda 11-23-10 | S. Fukuda 21-7-11
--- Other Racks --- | [21 empty] | S. Fukuda 21-7-11
Timing , 200V,0.5kW | Rack 10 | 1/38 m | Single Tunnel |  | 0.5 | [9 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | H. Hayano 9-8-09 | S. Fukuda 21-7-11
Cavity , 200V,3 kW | Rack 12 | 1/38 m | Single Tunnel | 2.95 | 2.05 | [9 empty] | 2.05 | 2.05 | 2.05 | 2.05 | 2.05 | 2.05 | H. Hayano 9-8-09 | S. Fukuda 21-7-11
Cryogenics, 200V, 2.1 kW | Rack 14 | 1/38 m | Single Tunnel |  | 2.1 | [9 empty] | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | H. Hayano 9-8-09 | S. Fukuda 21-7-11
BPM & Mag, 200V, 5 kW | Rack 16 | 1/38 m | Single Tunnel |  | 5 | 9.65 | [8 empty] | 5 | 5 | 5 | 5 | 6.93 | 5 | H. Hayano 9-8-09 | S. Fukuda 21-7-11
--- RF Loads --- | [18 empty] | 0 |  |  | S. Fukuda 21-7-11
Attenuator |  | None | [16 empty] | 0 |  | S. Fukuda 9-4-09 | S. Fukuda 21-7-11
Waveguides in service tunnel |  | None | [16 empty] | 0 |  | S. Fukuda 9-4-09 | S. Fukuda 21-7-11
Waveguides in penetration |  | None | [16 empty] | 0 |  | S. Fukuda 9-4-09 | S. Fukuda 21-7-11
Waveguides in beam tunnel |  | 13/38 m | Single Tunnel |  | 0.8 | [9 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | S. Fukuda 5-20-10 | S. Fukuda 21-7-11
Circulator with load |  | None | [16 empty] | 0 |  | S. Fukuda 9-4-09 | S. Fukuda 21-7-11
RF Loads |  | 13/38 m | Single Tunnel |  | 39.4499 | [9 empty] | 35.0338 | 30.4525 | 26.1474 | 21.919 | 30.6005 | 42.3 | S. Fukuda 5-20-10 | S. Fukuda 21-7-11
--- Other Loads --- | [18 empty] | 0 |  |  | S. Fukuda 21-7-11
Pulse motor for input coupler/tuner |  | (13+13)/38 m |  | 1.79 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | H. Hayano 9-8-09 | S. Fukuda 21-7-11
Vacuum Pumps |  | (1+1)/38 m |  |  | 0.63 | [9 empty] | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | H. Hayano 9-8-09 | S. Fukuda 21-7-11
HLRF related loss |  |  |  |  | 175.7933 | [9 empty] | 158.948 | 141.6725 | 125.2468 | 109.057 | 142.4405 | 159.9365
Fixed Loss in HLRF |  |  |  |  | 12.688 | [9 empty] | 12.688 | 12.688 | 12.688 | 12.688 | 12.728 | 12.688
Other Than HLRF |  |  |  |  | 11.645 | [9 empty] | 11.645 | 11.645 | 11.645 | 11.645 | 11.645 | 11.645
S. Fukuda 21-7-11
Subtotal RF unit Only |  |  |  |  | 200.9263 | [9 empty] | 184.081 | 166.8055 | 150.3798 | 134.19 | 169.8165 | 185.0695 |  | S. Fukuda 21-7-11 | 177.038
Total RF | [5 empty] | 11.015 | [16 empty] | 103390.2088
RF Component only Loads |  |  |  | 2.95
Note on A22: 1台当り