## Slide 1: ILC Utilities – Electrical / Mechanical
ILC has six regions:
  1/2. Sources (electron / positron)
  Damping Rings
  Ring to Linac
  SC Linac  Power critical
  Beam Delivery
But… Superconductivity means “low resistance”…

## Slide 2: Power Loads:
(Reference Design – 2006)
Beam Power (500 GeV): 22 MW

## Slide 3: Heat Loads:

## Slide 5: Superconducting resonators
Typical resonator intrinsic Q
Loaded Q – from coupler
losses
VCW
Vg
Vb
Pg
Te
VC
0
Tb
Cancel
Equilibrium ‘matched’ condition ideal

## Slide 6: Old RDR Power Distribution System

## Slide 7
Two 4-5 m diameter tunnels spaced by ~7 m.
Baseline Tunnel Layout
Accelerator Tunnel
Service Tunnel
Waveguides Cryomodules
Modulators Klystrons Electrical Dist Cooling System
Penetrations
(every ~12 m)

## Slide 9: Klystron Modulator:
150 KW (10/.6=17 MW peak) (XFEL 410KW)
Few % losses

## Slide 11: Installing an 8-cavity cryomodule:
~15 each made and tested DESY, Fermilab, KEK
(125 more now under construction)

## Slide 12: SC Linac power feed

## Slide 15: Top 3 load types:
Klystron/modulator localized 60%
Waveguide distributed 15% to be regulated
Cryomodule distributed 25%
Most of the heat load to water does not require tight temperature regulation

## Slide 16: Stacking of Loads / High Delta T
1 RF

## Slide 17: Stacking of Loads / High Delta T
1 RF

## Slide 18: Stacking of Loads / High Delta T
1 RF

## Slide 19
TUNNEL PENETRATION
KLYSTRON
MODULATOR
LLRF
ATTENUATORS
Heat Loss from Cryo ~5w/m (T.Peterson) ~(-0.18KW)
Heat Loss from RockWall ignored
Heat Loss (Air ) ~38 w/m ~(-1.3 KW) *15F delta T air at 2.5Km
Heat Gain (Waveguide) = 5.9 KW ~ +5.9 KW
--------------------------------------------- ----------------
NET LOAD to AIR (beam tunnel) + 4.42 KW
At Service Tunnel (to air -load to fancoil) = 1.17KW
At Penetration (water) = 0.676KW?
At Beam Tunnel (to air )= 5.9KW*
Assume issue with mixing air between tunnel, watercooled waveguide in the penetration by???
*if the straight run of waveguide in beam tunnel are watercooled, the remaining load to air becomes 5.4KW
Sealed
Sealed
cn eh Oct 4 2007
Waveguide Heat of ONE RF UNIT (Oct 4 2007)
See HVAC slides
later, for option of
aircooled wavgd
at penetration &
about rock contrbtion

## Slide 20: Klystron Cluster Concept
RF power “piped” into accelerator tunnel every 2.5 km
Service tunnel eliminated
Electrical and cooling systems simplified
Concerns: power handling, LLRF control coarseness
Same as baseline
~10 MW

## Slide 21: First Pass at New Tunnel Layout
RF Waveguide