## Slide 1: Electrical Power Load
AD & I
20 June, 2012
Marc Ross – for Emil Huedem (Fermilab)

## Slide 2: KCS Load Tables – 13.06.2012
e-
e+
DR
RTML
Linac
BDS
Dump
IR
Total
Thermal Load
Electrical Load
‘Peak Operating Load’ per system
System – by – System ‘worst case’ to be used to estimate equipment ratings

## Slide 3
For both main linacs:
Average rf power: 413 klystrons × 10 MW × 1.652 ms × 5Hz = 34.11 MW
Average beam power: 2 × 5.785 mA × 235 GV × 726.6 ms × 5Hz = 9.878 MW (28.96%)
wall plug–modulator pulse efficiency: ~90.3%
modulator pulse–HPRF efficiency: ~65%  wall plug – HPRF: ~58.7%
34.11 MW / 0.587 = 58.11 MW AC
58.11 MW(AC) – 9.878 MW(beam) = 48.23 MW cooling
Efficiencies:
.587 wall plug to rf
.85826 klystron to shaft
.80075 shaft to cavity
.4398 cavity to beam
.1774
AC Power and Heat Loads (KCS)
Low Power
17.0% efficient
0.5038  49.62% lost above ground: ~28.8 MW
0.3522  32.64% lost below ground: ~19.0 MW
17.0% into beam (dump): ~9.88 MW
~0.74% missing? ~0.43 MW
4.4% over?
1.06% extra rf units (3/282)
1.45% extra generated
 2.53% extra
Chris Nantista

## Slide 4: 500 GeV E_cm (5 Hz nominal)
e-
e+
DR
RTML
Linac
BDS
Dump
IR
Total
Thermal Load
Electrical Load
Reduce ‘Peak Operating Load’ per system 
5 Hz e- operation, longer damping cycle for e+
Approximate:
e- RF reduced half; cryo less: 0.8
RTML RF reduced ¼; cryo less 1.2
DR RF reduced ½; cryo 0.5MW 4.5
TOTAL reduction: 6.5 MW
162.5

## Slide 5: DR 5Hz/ 10Hz cryo
RDR numbers use 40W dynamic heat load per cavity - this has both beam and non-beam scaling contributions. They give 2.52 MW cryo plant capacity.
For the 5 Hz Low Power - beam currents are nominally the same as RDR and the DYNAMIC RF contribution to the cryo heat load should scale as number of cavities. This leads to an estimate (8 cavities per ring) of ~1.66 MW cryo plant capacity.
For 10Hz Low power (WHICH IS WHAT CFS WANTS, there's no simple scaling) - Number of cavities is 12 for the positron ring and 10 for the electron ring. However, the positron ring will only have
half the beam current, hence an adjusted power load which has not been calculated. For the moment, Vic has penciled in 2.1 MW as a placeholder.

## Slide 6
10 cavities, 54 wiggler magnets, on the e- side.
12 cavities, 60 magnets, on the e+ side.
Same unit static and dynamic heat loads as in the RDR.
One cryogenic plant provides all the damping ring cooling at 4.5 K and 70 K.
Same uncertainty and overcapacity factors as in RDR and same plant efficiency as in RDR.
Total installed plant size for all damping ring cryogenics (one cryogenic plant) is 1.45 MW.
Comparison with RDR (just for reference).
My conclusion for the RDR was two cryogenic plants at 1.13 MW each, for a total of 2.26 MW. (See RDR Table 3.8-3, which is consistent with the numbers in my spreadsheets.) So this present damping ring configuration requires 64% of the RDR damping ring power.