## Slide 1
Change Request Panel report
CR009 & CR014: Cryogenic Update
Mike Harrison, Vic Kuchler, Nick Walker
(with help from Hitoshi H, Tom P, Berndt P for CR009)

## Slide 2
Design Changes - cryogenics
Overview of request
The change request modifies the cryogenic plant layout from that proposed in the TDR. The main helium compressors and associated cryogenic storage tanks are moved from the underground cavern to the surface. An additional helium recovery compressor and backup power generator (1MW) is also added to recover the helium boil off from the cryomodules during a power outage or scheduled accelerator warm-up. A helium recovery line replaces a cryogenic transfer line. The proposed changes are shown schematically in figures 1 & 2. It is evident that the surface footprint is significantly larger and the tunnel cavern correspondingly smaller with these CR’s than the baseline design as described in the TDR.

## Slide 3
Design Changes - cryogenics

## Slide 4
Review Panel comments
The logistics of operations with the compressors on the surface are certainly improved (power, cooling, vibration, tunnel noise, maintenance, repair) the Panel find the most compelling reason for moving the compressors and liquid inventory is that of underground helium storage. Safety considerations of such a helium volume would impact many aspects of operation and make relatively routine operations such as maintenance essentially impractical.
Protecting the helium inventory during warm-ups, both planned and accidental, would also appear to be a crucial aspect of the system requirements which was not addressed in the TDR baseline. These CR’s rectify that omission.
Design Changes - cryogenics

## Slide 5
Review Panel comments
Since there are no natural supplies of helium in Japan all the helium needs to be imported. The consequences of a major loss of inventory could be very significant in both delayed operation and money. This issue was not addressed in the TDR but it is in these CR’s. The assumption is that any significant power outage would result in at least 6 hrs of refrigerator downtime. The proposed system would be scoped for emergency operation of up to 24 hrs with 50% gas and 50% liquid. With adjustments to the gas storage volume and generator fuel availability the system could easily operate for a longer period if deemed necessary.
Design Changes - cryogenics

## Slide 6
Review Panel comments: cost & schedule
It is difficult to quantify the cost impact of the CR’s since it is a significant change and the corresponding estimates in the TDR were generic rather than detailed. The proposals call for a significantly smaller underground enclosure, a significantly reduced tunnel heat load and a simplification of the cryogenic transport lines. All of these items will result in cost decreases, at a level potentially noticeable in the context of the ILC. On the other side of the ledger, the above ground footprint is larger, helium storage (both gas and liquid) is added, as is a 1MW emergency power generator, a gas compressor, and a small liquefier. Given the relative cost differential of above and below ground construction the expected cost impact is broadly neutral slightly tilted towards a cost reduction.
There should be no significant change to the schedule.
Design Changes - cryogenics

## Slide 7
Review Panel Conclusions
The change review panel recommends the CMB accept these CR’s.
The logistics of operations with the compressors on the surface are certainly improved (power, cooling, vibration, tunnel noise, maintenance, repair) the Panel find the most compelling reason for moving the compressors and liquid inventory is that of underground helium storage. Safety considerations of such a helium volume would impact many aspects of operation and make relatively routine operations such as maintenance essentially impractical.
Protecting the helium inventory during warm-ups, both planned and accidental, would also appear to be a crucial aspect of the system requirements which was not addressed in the TDR baseline. These CR’s rectify that omission.
Design Changes - cryogenics

## Slide 8
Review Panel Conclusions
In regard to environmental considerations the Panel notes that DESY cryogenic facilities are successfully operated in built-up areas of high population density and noise and vibration abatement has proven feasible. The same is true to a lesser degree with the RHIC cryogenic plant. With surface construction at the Kitakami site then the visual impact can be mitigated with some form of pit and associated landscaping. The details of this will depend on the exact location of the cryogenic penetrations and vary between the different locations.
The Panel notes in passing that there are actually two separate refrigerator systems at each location corresponding to the upstream and downstream cryo units. Although not present in the current design some form of interconnection could provide a level of redundancy in the case of equipment failure
The Panel believes that the CR will be broadly cost neutral but a new estimate will need to be made at some point. We predict there is minimal schedule impact.
Design Changes - cryogenics