## Slide 1: Detector Utility
2019/2/12
Yasuhiro Sugimoto
@ILD Integration Meeting

## Slide 2: CFS Schedule
By N.Terunuma

## Slide 3: CFS Schedule
If a positive statement by Japanese government is made, ILC basic design linked to CFS has to be fixed by 2019 summer
CFS Engineering Documents will be made in ~1 year based on this basic design
Based on the CFS Engineering Documents, CFS detailed design will be made by civil engineering companies in ~3 years
So, detector groups should clarify the requirements for the experimental hall and the utilities by 2019 summer

## Slide 4: Necessary utilities for detectors
Electricity
Heating, ventilation, air conditioning (HVAC)
Cooling water
Cryogenics for s.c. magnets
Chamber gas
(Network for data transfer)
Sub-detector assembly building
etc.

## Slide 5: Utility Survey
Requirements for utilities for sub-detectors were surveyed in 2018
  Electric power
  Cooling water
  Space
Two rounds of the survey were made, but only 5 sub-detector groups responded
  Vertex detector
  TPC
  ECAL
  SDHCAL
  AHCAL
Requirements for other sub-detectors will be supplemented by Y.S. to estimate total necessary electric power and cooling water
  Power consumption by sub-detectors is relatively small compared to magnet power
  So, rough estimate on the sub-detector power consumption is OK

## Slide 6: Utility Survey
6 items for electricity/cooling water
PFE : Power consumption of sub-detector Front-end Electronics
QD : Heat loss in sub-det. (= PFE )
QPC : Heat loss in power cables
PLV : AC power input to LV PS
e : Efficiency of LV PS (PLV*e= PFE +QPC)
QLV : Heat loss in the LV PS (=(1-e)*PLV)
PBE : AC power input to back-end elec./HV power supply
QBE : Heat loss in the BE/HV PS (=PBE)
PCS : Electric power to drive the cooling system
QCS : Heat to be extracted from cooling system (= QD +PCS)
Type of
cooling
water
Extracted by cooling water
Electric Power
Heat loss to air
Cooled by FCU

## Slide 7: electricity

## Slide 8: Basic concept
On surface: 275(154)kV  (66kV)  6.6kV
6.6kV AC is sent to underground USC through Utility Shaft
In USC: 6.6kV  400(3f) / 200(3f,1f) / 100V(1f)
Power dissipation is eventually extracted by cooling water ( cooling tower on surface)

## Slide 9: Tentative estimation for ILD
Sub-detectors:
Y.S.’s guess (based on TDR description, if exists) except for HCAL, ECAL, TPC, and VTX
Not listed:
Infrastructure in assembly halls
Computers for rec/ana/sim.
Office building
Cooling tower and chiller on surface
Item |  | Power (kW) |  |  | 
QD0/QF1/Crab cavity | Power supply | 150 |  |  | 
 | Cold box | 150 |  |  | 
 | He Compressor | 300 | (Surface) |  | 
Detector Solenoid | Power supply | 250 |  |  | 
 | Cold box | 50 |  |  | 
 | He Compressor | 500 | (Surface) |  | 
Sub-detector | Total | 161 | FEE | BEE | Cooling
 | Muon | 12 | 5 | 5 | 2
 | HCAL | 45.5 | 27.5 | 8 | 10
 | ECAL | 40 | 20 | 12 | 8
 | VFC | 9 | 2 | 5 | 2
 | SET | 9 | 2 | 5 | 2
 | TPC | 16.2 | 15 | NA | 1.2
 | SIT | 8 | 1 | 5 | 2
 | FTD | 8 | 1 | 5 | 2
 | VTX | 13.5 | 2 | 1.5 | 10
Computer farm |  | 1000 | (Surface) |  | 
Water pump |  | 25 | (11kWx2+3.7kW) |  | 
HVAC |  | 600 | (Surface, CMS) |  | 
Lighting |  | 25 |  |  | 
Air compressor |  | 50 | (Surface) |  | 
Platform mover |  | 100 |  |  | 
Crane for ILD | 5t x 3 | 21 |  |  | 
 | 40t | 50 |  |  | 
Total |  | 3432 |  |  | 
Underground |  | 1282 |  |  | 

## Slide 10: Comparison with other study
He compressor is not included in SiD Detector Solenoid
Cranes and lighting are not included in SiD DH utility
CMS and CLIC data is taken from LCD-Note-2013-011
 | CMS | CLIC | SiD | ILD
Detector Solenoid | 900 | 900 | 294 | 800
QD0/QF1/CC | NA | NA | NA | 600
FEE | 600 | <10 | 12 | 75
BEE | 650 | <10 | 70 | 47
PC farm | 800 | 1000 | NA | 1000
DH utility | NA | NA | 105 | 246
Cooling | 850 | 750 | NA | 65
HVAC | 600 | 600 | NA | 600
Sum | 4400 | 3250 | 481 | 3432

## Slide 11: Cooling water

## Slide 12: Basic concept
Two types of water are supplied from surface
  Normal temp. water: T~30 ℃, DT~10 ℃
  Chilled water: T~10 ℃, DT~5 ℃ (TBD)
  High pressure due to Dh~100m can be isolated by heat exchangers in USC
Sub-detectors are cooled by sub-detector cooling systems
  Coolant could be CO2, water, air, or something else
  Sub-detector cooling systems are cooled by cooling water
Electronics racks are cooled by fan-coil units
  Cool air flow generated by chilled water removes heat, and returns to room temperature

## Slide 13: Schematic
Surface
Underground
~30℃
~40℃
~10℃
~15℃
Chilled water
Fan-coil units (electronics racks)
Sub-det. Cooling systems
Normal temp. water
Sub-det. Cooling systems
Low-conductivity water
r>1MWcm
Magnet power supply

## Slide 14: Requirement
Cooling water for underground facilities
 |  | Chilled Water |  |  | Low-conductive Water |  |  | Normal Water |  |  | 
Item |  | Heat (kW) | dT | Flow (L/min) | Heat (kW) | dT | Flow (L/m) | Heat (kW) | dT | Flow (L/m) | 
QD0/QF1/CC | Power supply |  |  |  | 150 | 10 | 214 |  |  |  | 
 | Cold box |  |  |  | 150 | 10 | 214 |  |  |  | 
Detector Solenoid | Power supply |  |  |  | 250 | 10 | 357 |  |  |  | 
 | Cold box |  |  |  | 50 | 10 | 71 |  |  |  | 
Sub-detector | Muon | 12 | 5 | 34 |  |  |  |  |  |  | 
 | HCAL | 45.5 | 5 | 130 |  |  |  |  |  |  | 
 | ECAL | 40 | 5 | 114 |  |  |  |  |  |  | 
 | VFC | 9 | 5 | 26 |  |  |  |  |  |  | 
 | SET | 9 | 5 | 26 |  |  |  |  |  |  | 
 | TPC | 3 | 5 | 9 |  |  |  | 13 | 5 | 38 | NW for precision chiller
 | SIT | 8 | 5 | 23 |  |  |  |  |  |  | 
 | FTD | 8 | 5 | 23 |  |  |  |  |  |  | 
 | VTX | 13.5 | 5 | 39 |  |  |  |  |  |  | 
Pump |  | 11 | 5 | 31 | 11 | 10 | 16 | 3.7 | 5 | 11 | 
Cubicle (AC transformer) |  | 64 | 5 | 183 |  |  |  |  |  |  | 95% efficiency, FCU
Total |  | 223 |  | 637 | 611 |  | 873 | 17 |  | 48 | 
Primary Loop |  | Chilled Water |  |  | Normal Temperature Water |  |  |  |  |  | 
 |  | 637 |  |  | 921 |  |  |  |  |  | 

## Slide 15: hvac

## Slide 16: HVAC
Air handling units on surface (next to assembly hall)
Air ducts through main shaft
Necessary capacity has not been studied yet

## Slide 17: HVAC - CMS

## Slide 18: HVAC – Assembly Hall
Garage for air handling units

## Slide 19: Other services

## Slide 20: Chamber gas
Chamber gas is necessary for TPC and SDHCAL
Gas storage on surface: 8x4m2 for each
Gas system underground
  TPC: Some space on the platform
  SDHCAL: 4x4m2 space in USC and small space on service gallery and platform
CMS RPC gas system

## Slide 21: LASER system
Laser system will be used for tracker alignment
Laser light source requires isolated space for safety reason

## Slide 22: space

## Slide 23: Location of Utility/Service
Platform
Low-voltage power supply
Cryogenics for magnet
Etc.
Service gallery
Electronics racks
Magnet power supply
Utility/Service Cavern
AC transformer
Heat exchangers/pumps for cooling water
Sub-det. Cooling systems
LASER/Gas system
QF1 cryogenics
Workshop
WC
Surface
He/Air compressors
HVAC
Gas storage
PC farm (?)
Cooling tower/chiller
Utility Shaft
Main Shaft
Electricity, cooling water, elevator
He, Chamber gas,
Optical fibers, Air ducts

## Slide 24: Utility/service cavern
Tentative design
Utility Shaft
Detector Hall
Main Shaft

## Slide 25: Detector Platform
: Space for electronics racks

## Slide 26: Service Gallery
2F is just a path to platform
3F-5F are used for electronics racks
6F is for magnet power supply

## Slide 27: Service Gallery
2F

## Slide 28: Service Gallery
3-5F

## Slide 29: Service Gallery
6F

## Slide 30: Space requirements
People tends to like electronics rack space on the platform, where
  few 100 G leakage field could exists
  access may not be allowed during experiment
Because space on the platform is limited, there could be severe competition between sub-detectors

## Slide 31: Pre-assembly hall
In addition to the main assembly hall on surface, we need pre-assembly hall for sub-detector assembly
Requirements from sub-detector groups were collected/estimated since 2015
Sub-detector | Area (m2) | Building
Iron yoke blocks | 900 (=20x45) | Yoke assembly building attached to Main AH
SDHCAL/AHCAL | 1400/330 | Independent Pre-Assembly Hall at IR Total 3000/1930 m2 FCAL should use HCAL space after HCAL installation
ECAL | 830 | 
Muon detector | 400 | 
TPC | 100 | 
Si detectors | 100 | 
Utility | 170 | 

## Slide 32: Summary
ILD requirements for utilities have been surveyed to some extent
For the moment, it seems power consumption of sub-detectors are relatively small compared to magnet power
Because the estimation for each sub-detector still has large uncertainty, total power consumption of sub-detectors should be describe in IDR
Service gallery and Utility/Service cavern which we propose seem to have enough space for ILD
Detail of space requirements is still too premature to be described in IDR
There are still many items of requirements for detector utilities to be clarified to fix the CFS design in interaction region