## Slide 1
Recent CFS activity in Japan
Nobuhiro Terunuma, KEK

## Slide 2: Background of Civil Engineering Design
Design of accelerator tunnels and detector hall has been conducted by the international working groups under GDE and LCC.
Site specific design, especially for facilities on ground and its connection to the accelerator, has been conducted by the working group under the Tohoku ILC planning office.
Comprehensive civil engineering integration is underway by the CFS team from KEK and Tohoku ILC planning office. The draft will be discussed with the international ILC-CFS working group.

## Slide 3: Recent Activity on CFS in Japan (1)
The design group has been enhanced to create a basic planning document that serves as input for basic and detailed designs during the preparation phase.
  It consists of members from the KEK ILC Group, KEK Facility Department, and Tohoku ILC Research Group.
AAA (Advanced Accelerator Association)
  Working group has been established to support CFS design, particularly for groundwater treatment, beam dump civil design, and earthquake resistance.

## Slide 4: Recent Activity on CFS in Japan (2)
ILC Facility Evaluation Subcommittee of the Rock Mechanics Committee, the Japan Society of Civil Engineers
  Evaluate the validity of ILC civil engineering design at the Kitakami candidate site from the viewpoint of rock dynamics.
  Closed committee because it includes the site specific confidentials.
  Expect a report will come by March 2020.
  Note: 2012, Guidelines for the civil engineering work of International Linear Collider (ILC) facilities; Rock Mechanics Committee in Japan Society of Civil Engineers. It was the subcommittee for the establishment of standard specifications for the civil engineering work of Internal Linear Collider

## Slide 5
We are collecting and integrating drawings for the CFS basic plan.
Note! These are drafts for checkout.

## Slide 6
for Discussions

## Slide 7
Main Linac (ML) tunnel
ML section is about 70% of the ILC-250 (end to end).
Follow the geoid
Central radiation shield will be put after finishing the tunnel.
RF power station
Beamline
1.1m from
floor
?
9.5 m
5.5 m
1.5 m
1 m
Notes: 左下のブロックを消す

## Slide 8
Where does RTML pass through the ML tunnel?
TDR Vol3,
p167
The upper left figure is often used after the change request of central wall reduction.
It was prepared only for discussion of equipment layout and its layout has not been determined.
In particular, RTML is above the waveguide and is higher than that of TDR.
    It is misleading and brings many considerations on beam dynamics, installation and alignment.
RTML position in the current optics design has never changed from TDR.
This figure should be modified.
Notes: 左下のブロックを消す

## Slide 9
Handling of groundwater outside the tunnel
Inflow water assumption
・1.0 tons/min/km (max)
・5.0 tons/min/Access Point (max)
About 30,000 tons/day
Pump-up to the surface;
Supplemental water for cooling tower
To access hall
Draw water into the access hall tank
  Natural flow scheme
  Pump relay scheme
Rey.Hori / KEK

## Slide 10
ML tunnel Will be extended beyond the turn-around;
Make a future extension of ML easily.
Enhance the safe evacuation of turn-around.
91 m
Tune-up beam dump
56 m
4.5 m
4.0 m
ML tunnel
Turn-around
1.65 m
9.5 m
5.5 m
RTML
ML

## Slide 11
1.3 km
Layout of Central Region
100 m
Main Beam Dump
Surface facility for IP
Surface facility for DR
Tune-up Dump
0.5 km
Damping Ring
IP
Detector Hall
Main Beam Dump
Tune-up Dump

## Slide 12
Damping Ring
Arc Section
4.7 m
6.5 m
Positron
electron
Positron
Straight Section
13 m
6.9 m
Circumference: 3.2km
Start with two rings
The arc section of the ring is a single tunnel without a central shield.
Straight section is Kamaboko with a 3.5m central shield. (TDR)
Rey.Hori / KEK

## Slide 13
5.5 m
11 m
BDS
BDS
Damping Ring
300 m
300 m
LTR/RTL
Between DR and BDS tunnel
Beamlines
  Injection to DR
  Extraction from DR with tune-up dump
  Spin rotator
TDR design:
  Kamaboko with 3.5m central shield
  Do we need it?
Check the requirements and optimize the design
Rey.Hori / KEK

## Slide 14
DR beam dump
(electron)
Positron
spin rotation
RTML
electron
(positron)
BDS (electron)
(electron)
Damping Ring
Example:
Electron ML side
IP

## Slide 15
ChangeRequest-015: Single tunnel for e+ BDS (TDR was two tunnel scheme.)
From the construction point of view, it is desirable to simplify the design.
  Discussion has been started by the CFS group in Japan.
  The 11m-wide kamaboko tunnel along the BDS beamline is a candidate.
BDS tunnel (PM-8 to PM+8)
CR-015: Fig.5 tunnel cross-section model for cost estimation
Example: electron BDS; downstream of undulator
PM-8
PM+8

## Slide 16
Positron Source
Scheme selection will be done by the end of the first year of preparation phase.
Prepare the CFS design for all possible schemes.
For undulator scheme, draft CFS design exists as that for BDS.
For e-driven schemes, CFS design will be conducted by following the current discussions, for example, the separate dedicated tunnel for flexible construction/commissioning strategy .
Tunnel options for e-driven: T.Omori, LCWS2018

## Slide 17
Detector Hall
12 m
SiD検出器, 重量 8,000t
11 m
16 m
13 m
Vertical Shaft for Detector (diam. 18m )
4000t Crane
Utility Shaft
（diam. 10m）
IP
Damping Ring
BDS (electron)
40 m
133 m
25 m
ILD検出器, 重量 15,000t
BDS (positron)
Utility
floors
Layout of the detector hall and around is under discussion with MDI
Rey.Hori / KEK

## Slide 18
96m
160m
11m
4m
Plan view of the Detector Hall
100m
300m
Damping Ring
Straight section
Distribution of 66kV
Access tunnel
ELTR/PRTL
Electron injection
Positron extraction
BDS (electron)
PLTR/ERTL
Positron injection
Electron extraction
BDS (positron)
Distribution of 66kV

## Slide 19
Main beam dump
Big cavern to install the 5m-thick shields.
Water dump capable for 18MW beam power (1TeV).
Enable the future de-commissioning
22 m
16 m
25 m
70 m
25 m
Radiation Shield
Beam dump
Cooling system

## Slide 20
20 m
14 m
25 m
50 m
Dump room
with 4m thick concrete bed
Tunnel cross section will be simplified.
Tune-up beam dumps
60kW (9 points) and 400kW (2 points)
ML tunnel

## Slide 21
H. Hayano, LCWS2017, Strasburg
Rey.Hori / KEK

## Slide 22
H. Hayano, LCWS2017, Strasburg

## Slide 23
H. Hayano, LCWS2017, Strasburg

## Slide 24
H. Hayano, LCWS2017, Strasburg
TDR
Tohoku study
  Smaller volume
  Separate cavern by function

## Slide 25
H. Hayano, LCWS2017, Strasburg

## Slide 26
H. Hayano, LCWS2017, Strasburg
An example of access tunnel arrangement:
It shows how large space is required for pipes and cables.
The actual layout must be determined by considering various backgrounds.
Transport
Cold Box (diam. 4m)
Into access hall
In installation, repair(?) and addition for future extension of ILC